# DORMA SPECIFICATION SERVICES

Project

L20/			LOW ENERGY SWING DOOR OPERATORS

Manufacturers		DORMA UK LTD.

WILBURY WAY, HITCHIN, SG4 0AB.

Tel: 	+44 (0)1462 477 600,

Email: 	info.gb@dormakaba.com

Web: 	www.dormakaba.co.uk

Operating System	ED100/250LE Surface Applied Low Energy Swing Door Operator

    - Tested and certified to 1,000,000 operation cycles

    - Integrated ESM Energy Saving Mode function which allows the sensors to be switched to standby to minimise unnecessary power (Up to 30% power saving)

    - Drive unit encased in purpose designed extruded aluminium profile

    - 70 (H) x 130 mm (D) x 700 (W)

    - Electromechanical automatic drive unit consisting of a DC motor, multi-stage gearing, spring and modular designed electronic control system

    - Adjustable electronic control system to overcome doors seals or latch action locking devices during the closing cycle.

    - Certifire tested (Certificate available on request)

    - Mainly closes via spring force with direct drive technology to power close minimising energy loss

    - Steplessly adjustable closing force EN 1154 between (EN 2 – 4 ED100)  (EN 4 – 6 ED250)

    - Adjustable opening speed

    - Hold open time adjustable between 0 and 30 seconds

    - 4 position mode switch (off, automatic, hold open, exit only)

Accessible Toilet Pack

    - Wireless wall switch actuation (150mm x 150mm) satin stainless steel complete with radio Control

    - TV lock and internal locking switch

    - Emergency green break glass

Power Failure/Fire Alarm	In the event of power failure door reverts to spring controlled manual operation

Safety Devices

    - Prosecure Opti Safe tested safety sensors fitted to opening and closing side of each door leaf (Option)

    - Framed glazed safety barrier with toughened glass infills installed along the line of doors in the open position (Option)

    - DORMA Pivotsafe/Hingesafe anti finger trap device (Option)

    - Self-regulating safety system monitoring all door movements including closing force

Operator Cover

    - Silver Anodising Aluminium (Option)

    - Polyester powder coated to a standard RAL colour (Option)

Applicable Standards	The installation shall comply with BS EN 16005

Electrical Requirements 	The electrical contractor shall provide a 240-volt AC mains spur to the right-hand side of the opening above and on the same face that each drive unit is fitted. The spur must be switched and fused with a central flex outlet faceplate. A 10 amp residual circuit breaker at the mains board and a 5-amp fuse at the spur shall protect the circuit.

Real Time Remote	Dorvision GPRS based wireless system concealed within the operator; system shall

Monitoring System	monitor each door location remotely via the internet incorporating facility to lock / unlock doors, timed automatic locking, reset, diagnostic system check and to provide data capture on usage and performance (Option)