# DORMA SPECIFICATION SERVICES

Project

L20/			AUTOMATIC CURVED SLIDING DOORS

Manufacturers		DORMA UK LTD.

WILBURY WAY, HITCHIN, SG4 0AB.

Tel: 	+44 (0)1462 477 600,

Email: 	Info@dorma-uk.co.uk

Web: 	www.dorma.com

Operating System	DORMA BST Automatic Curved Sliding door system consisting of curved ES200 automatic sliding door operator, toughened glass fixed side screens and door leaves

(SECECT ONE OF THE FOLLOWING)

    - Full Circle 360

    - Half Circle 180

    - Segmental

    - Tested and certified to 1,000,000 operation cycles

    - Night/Bank Facility for first and last entrance

    - 5 position mode switch (off, automatic, partial opening, exit only and hold open)

    - Drive unit encased in purpose designed extruded aluminium profile

Activation

    - DORMA Prosecure Opti Combi combined radar activation and threshold infrared safety sensor

    - Link to access control (By others). DORMA require a normally open volt free contact momentarily closed on receipt of a valid signal from the access control system (Option)

Power Failure/Fire Alarm	Monitored battery back up system to automatically open the doors in the case of a power failure or upon a signal from the interfaced fire alarm system

Break Out Facility		Not available

Safety Devices

- Self-regulating safety system monitoring all door movements including closing force.

- Auto reverse function if the doors make contact with an obstruction during the opening cycle

- Emergency Break Glass (Option)

Doors and Screen Work

    - Door leaves constructed from toughened safety glass incorporating fine frame profiles

    - Fixed side screens constructed from toughened safety glass incorporating fine frame profiles and surrounding glazing channel

Aluminium Profile coating

    - Polyester Powder Coating (Option)

    - Silver Anodised (Option)

Locking Facility 		Electrometrical concealed within the operator (Option)

Applicable Standards	The installation shall comply with BS: EN 16005

Electrical Requirements 	The electrical contractor shall provide a 240-volt AC mains spur to the right-hand side of the opening above and on the same face that each drive unit is fitted. The spur must be switched and fused with a central flex outlet faceplate. A 10 amp residual circuit breaker at the mains board and a 5-amp fuse at the spur shall protect the circuit.

Fire Alarm Requirements	The fire alarm specialist shall provide a normally open volt free contact that is closed on alarm. The contacts shall be terminated adjacent to the fused spurs

Real Time Remote	Dorvision GPRS based wireless system concealed within the operator; system shall

Monitoring System	monitor each door location remotely via the internet incorporating facility to lock / unlock doors, timed automatic locking, reset, diagnostic system check and to provide data capture on usage and performance (Option)