# DORMA SPECIFICATION SERVICES

Project

L20/			AUTOMATIC SLIDING DOORS

Manufacturers		DORMA UK LTD.

WILBURY WAY, HITCHIN, SG4 0AB.

Tel: 	+44 (0)1462 477 600,

Email: 	Info@dorma-uk.co.uk

Web: 	www.dorma.com

Operating System	DORMA ST-Flex Green thermally broken, fine framed, double glazed automatic door system Tested system ‘U’ value between 1.4 and 1.8 W/m2K

    - ES200 Microprocessor controlled, modular designed Automatic sliding door operator

    - Tested system ‘U’ value between 1.4 and 1.8 W/m2K

    - Tested and certified to 1,000,000 operation cycles

    - Night/Bank Facility for first and last entrance

    - 5 position mode switch (off, automatic, partial opening, exit only and hold open)

    - Drive unit encased in purpose designed extruded aluminium profile

      - 100mm (h) (Option)

      - 150mm (h) (Option)

Activation 		Entry:

Exit

    - DORMA Prosecure Opti Combi combined radar activation and threshold infrared safety sensor

    - Hard wired or wireless wall switch actuation satin stainless steel 150 x 150mm (Option)

    - Slimline jamb switch satin stainless steel 115 x 45mm (Option)

    - Link to access control (By others). DORMA require a normally open volt free contact momentarily closed on receipt of a valid signal from the access control system (Option)

Power Failure/Fire Alarm	Monitored battery back up system to automatically open the doors in the case of a power failure or upon a signal from the interfaced fire alarm system

Break Out Facility		NA

Safety Devices

- Self-regulating safety system monitoring all door movements including closing force.

- Auto reverse function if the doors make contact with an obstruction during the closing cycle (infrared threshold safety sensor)

- Emergency Break Glass (Option)

- Rear Edge Safety

      - Full height frameless pocket screens constructed from 10mm toughened safety glass and patch fittings

      - 900mm high all glass solid infill safety barriers

      - DORMA Prosecure Opti Scan Rear Edge Presence Sensors reducing the door to “Low Energy Speed” upon activation

Doors and Screen Work

    - Door leaves and fixed side screens constructed from double glazed toughened or laminated glazing in fine framed profiles

Aluminium Profile coating

    - Polyester Powder Coating (Option)

    - Silver Anodised (Option)

    - Stainless Steel (Option)

Locking Facility

    - Electromechanical concealed within the operator (Option)

    - Manual Bottom locking with euro profile keyed cylinder/thumb turn (250mm per door leaf reduction in clear opening) (Option)

Applicable Standards	The installation shall comply with BS EN 16005

Electrical Requirements 	The electrical contractor shall provide a 240-volt AC mains spur to the right-hand side of the opening above and on the same face that each drive unit is fitted. The spur must be switched and fused with a central flex outlet faceplate. A 10 amp residual circuit breaker at the mains board and a 5-amp fuse at the spur shall protect the circuit.

Fire Alarm Requirements	The fire alarm specialist shall provide a normally open volt free contact that is closed on alarm. The contacts shall be terminated adjacent to the fused spurs

Real Time Remote	Dorvision GPRS based wireless system concealed within the operator; system shall

Monitoring System	monitor each door location remotely via the internet incorporating facility to lock / unlock doors, timed automatic locking, reset, diagnostic system check and to provide data capture on usage and performance (Option)